4 types of ground (ARRL handbook 2010 28.1.8)
1 - Electrical Safety Ground (bonding)
2 - RF Return (antenna ground)
3 - Common reference potential (chassis ground)
4 - Lightning and transient dissipation ground
(See IEEE Std 110-2005 for in depth details)

Keep in mind NEC is concerned with SAFETY – not performance. Legal goal is comply and be safe, while performing well at the same time, with the same equipment. Hence the ‘4 grounds’ may use common equipment, even though differing criteria or goals

Regardless of intent, purpose or design – ALL GROUNDS MUST BE BONDED

* Safety Ground (Bonding)
Commonly seen as the ‘green wire’ or ‘third prong’
NEC requires all to be bonded – also good engineering practice
Power Service: used as path to trip over current protection
 So, what is bonding?
Connecting all together so no voltage differential exists
All rise and fall together
It’s voltage differential that allows for current flow – damage

A good conductor at 60hz is often high impedance at RF
may also become a good RF RX antenna

* RF Ground
Things like Enclosures or ground planes on PCBs
Modern circuits are much more sensitive to millivolt signals
Should be using equipment enclosures or shielded conductors as parts of RF circuits
Instead systems create a common reference plane and keep all connected to a common potential

* Lightning Dissipation Ground
THE Standard is Motorola’s R-56 Site Standard
Available online, legally
Over 500 pages
I won’t even TRY to cover 500 pages in one sitting!!
Crux of the goal:
Everything needs to be setup so as voltages rise/drop – EVERYTHING rises at the same time
Voltage differential is how you get current flow
No differential – no flow, regardless of charge
Talk example of cows near a strike
Parallel vs perpendicular
Rough outline:
Tower Grounded at each leg – with halo
Antenna connector – surge arrestor bonded to tower ground (not tower)
As feedline transistions to horizontal and leaves tower – another arrestor
As feedline enters building – another arrestor
All halos, arrestor grounds entrance grounds are bonded
This ground system is also bonded to ‘Neutral ground point’ not neutral itself
Common ground panel outside building – internal ground panels bonded to this
Exterior ground panel bonded to grounds, halos and feeds. Design goal:

As ground, building, tower, antenna or feedline voltages increase or decrease – they all do so together at the same time. Do not use tower for ground line – unreliable

Be aware of dissimilar metals and need for ‘Alluminox’ or other conductive barriers on ALL joints, connections

RF part of Feedlines being the exception – ensure adequate weatherization

ALL conductors (except power) must be fitted with surge arrestors and those arrestors bonded to panels/ground. Rotors, Ethernet, telepone, I-net, etc